Operations Manual

Deployment, Verification and Incident Handling

Prepared 2026-03-09

Table of Contents

Tip: If the page numbers are stale, update the TOC field after opening the file.

# Technical Baseline

| Metric | Target | Notes |
| --- | --- | --- |
| Input Power | 100-240V AC, 50/60Hz | Single PSU supported; dual PSU optional |
| Typical Draw | 42W | Measured under nominal traffic |
| Peak Draw | 68W | Transient during startup |
| Operating Temp | 0°C to 40°C | Derate above 35°C in closed racks |
| Storage Temp | -20°C to 60°C | Avoid rapid thermal cycling |
| Humidity | 10% to 90% RH | Non-condensing |

Commissioning Checklist

1. Confirm node identity, rack location, and management label before activation.

2. Validate clock source and NTP sync status before connecting upstream services.

3. Record baseline CPU, memory, and I/O values for post-change comparison.

4. Capture rollback command set and escalation contacts in the change record.

# 1. Scope and Intended Environment

This manual is intended for deployment engineers and operations staff responsible for commissioning, daily monitoring, and first-line diagnostics.

The procedure assumes stable power input, controlled temperature, and a managed network segment with documented addressing rules.

# 2. Installation Workflow

Run a pre-flight check before rack-mounting: package integrity, accessory count, grounding path, and cable plan must all be confirmed.

After physical setup, perform baseline verification in this order: power-on self-check, network reachability, service registration, and alarm channel validation.

# 3. Routine Maintenance

Weekly tasks include health snapshot export, resource trend review, and backup consistency checks.

Monthly tasks include firmware advisory review, capacity delta analysis, and incident postmortem updates to the operating runbook.

# 4. Incident Playbook

| Symptom | Likely Cause | Recommended Action |
| --- | --- | --- |
| Power LED remains off | No upstream power or unstable input | Validate PDU output and reseat power cable |
| Management endpoint unavailable | Address conflict or gateway mismatch | Restore known-good network profile and verify ARP table |
| Sustained thermal warning | Blocked airflow path | Remove obstructions and verify fan health |
| Service starts but drops | Dependency timeout | Inspect startup logs and extend service warm-up threshold |

Support Channel: ops-support@example.com